## LOADS SHEET
PROJECT : PROPOSED WOODS VILLAS PROJECT
TITLE : ELECTRICAL LOAD PARTICULARS SHEET
DATE:01-06-2026
EB LOADS
S.NO | FROM | TO | No.Of Villas | CL LOAD in KW for Villa | CL LOAD in KW
1 | MAIN PCC PANEL | FEEDER PILLAR-1 (1-12,12A) | 13 | 3 | 39
2 | MAIN PCC PANEL | FEEDER PILLAR-2 (19-30) | 12 | 3 | 36
3 | MAIN PCC PANEL | COMMON SERVICES PANEL |  |  | 45
120
3 | MAIN PCC PANEL | FEEDER PILLAR-3 (14-18+31-37) | 12 | 3 | 36
4 | MAIN PCC PANEL | FEEDER PILLAR-4 (38-53) | 16 | 3 | 48
84
| TOTAL LOAD |  | 53 |  | 204
| Diversity factor 75% Total Load in KW |  |  |  | 153
| By applying a power factor of 0.9 on the overall load, the continuous load in would be in KVA |  |  |  | 170
Recommended size of the Transformer would be 2nos.100 KVA,11kV/433V outdoor CSP Transformer.
DG LOADS
1 | DG PANEL | COMMON SERVICES PANEL |  |  | 35
2 | DG PANEL | CLUB HOUSE PANEL |  |  | 35
70
| Assuming a load factor of 80% and power factor at 0.8, total Load would be |  |  |  | 109.375
Recommended size of the D.G Set would be 100 kVA, 415V, 0.8 pf D.G Set with acoustic